Hydrocarbon Liquid Leak Detection System

SPECIFICATION

---

Industrial Applications

- General

Furnish a complete hydrocarbon leak detection system, including electronic alarm module, hydrocarbon sense cable, and accessories. The system shall detect and locate liquid hydrocarbon leaks along full length of sense cables to give continuous protection to the critical areas of the Project Facilities [Installation to be specified, i.e. pipelines, storage tanks, airport distribution networks] from the risk of [hydrocarbon] [non-conductive] liquid leaks.

The system manufacturer shall have at least ten years of experience with leak detection and location technology, including both sense cable and the associated alarm electronics.

- Overall System

The liquid leak detection system shall be able to locate multiple [hydrocarbon] [non-conductive] liquid leaks simultaneously as well as cable break faults (one per sensor).

TTK  -  Type: FG-OD

CE 0081        II 1G

Ex ia IIB T4 Ga

LCIE 13 ATEX 3082 X

IECEx LCIE 13.0072X

The system shall be compliant to hazardous atmosphere locations in ATEX zones 0, 1 and 2, sense cable shall be intrinsically safe for gases of groups IIA and IIB, tested to Standard IEC 60079, IECEx approved by a recognized worldwide third-party certification body.

ATEX / IECEx Marking:                                                            -30°C < T < +100°C

- Type

The detection system shall be composed of the following elements:

- FG-NET-LL digital monitoring unit, manufactured by TTK, or equivalent,

- FG-BBOX-LL satellite device (if required), manufactured by TTK, or equivalent,

- FG-ODxx or FG-ODLxxyy addressable sense cables (where xx is the section length (= distance between micro-processors) in meters and yy is the number of sections in one string), manufactured by TTK, or equivalent,

- Jumper cables and all required ancillary equipment.

- Sense Cable

  - Performances

The hydrocarbon sense cable shall detect the presence of diesel, gasoline, crude oil, jet fuel and other liquid hydrocarbons.

The hydrocarbon sense cable shall ignore water and be insensitive to small pollutions, dirt and external loads.

The cable shall be reusable after leak detection.

  - Construction and Certification Requirements

Each sense cable shall:

- have an embedded microchip circuit allowing the transmission of an addressable signal to the digital monitoring unit,

- be connected via male and female connectors,

- be made of light and flexible material in an easily identifiable color,

- undergo to a mostly reversible [hydrocarbon] [non-conductive] liquid absorption, allowing for absorbed liquid to be cleaned with appropriate solvent,

- be certified for safe use in ATEX Zone 0, protection mode “IA” (intrinsically safe), Group IIB, Temperature Class T4.

- System Capacity

The monitoring unit shall be capable of monitoring at least 120 sense cables directly connected (that’s 2 400 meters), and up to 1 000 sense cables (that’s 20 000 meters) connected via satellite units (FG-BBOX-LL or equivalent).

If the cables have to be installed in a classified (explosive) area, a Zener Barrier device shall be used.

The monitoring unit shall be able to show all the cables connected and group them by zone.

The monitoring unit shall be able to monitor three independent circuits of sense cables.

- Digital Monitoring Unit

The digital monitoring unit shall receive data processed and transmitted by each sensor as well as raising the alarm. It shall be supplied from the same supplier as the sense cables.

Contact with liquid shall result in an audible and visual alarm, activation of an output relay, and shall notify the user in distance by remote monitoring.

  - Multiple leaks

The electronic alarm module shall continue to monitor the sense cable after detection of liquid. It shall re-alarm if the liquid spreads or migrates beyond the initial section in leak alarm, or if a second leak is detected on another section, at any location along the sensing circuit (see figure 1). The monitoring system shall be able to detect as many leaks as the number of sections are installed, and capable of revealing the expansion of the leak.

Figure 1: Simulation of multiple leakages on the monitoring unit

  - Cable break fault

The complete system shall be continuously monitored for electrical continuity. The loss of continuity in any of the wires shall result in an audible alarm, illumination of an alarm LED, and actuation of an output relay. The system shall be capable of identifying the section of smart sense cable where the continuity is lost.

  - Interface

There shall be 8 configurable dry contacts (relays) available in the system to enable remote monitoring and control. Any interruption in power shall be indicated by a specific dry contact.

RS-232, RS-422/485 serial ports with Modbus/Jbus communication protocol shall be available on the digital monitoring unit.

An Ethernet port shall be available on the monitoring unit.

Integrated maps of the leak detection installation highlighting the location of the fault shall be able to be displayed on the monitoring unit.

Email notification, remote monitoring functions shall be available on the monitoring unit.

The digital monitoring unit shall be the model FG-NET manufactured by TTK S.A.S., or equivalent.

- Jumper cable connection and ancillary equipment

- Jumper cable shall be available to interconnect sense cable sections or to facilitate remote mounting of the electronic alarm module.

- Installation

For pipelines application, the sense cables shall be installed along the entire length of the pipeline to be monitored.

The monitoring units shall be located in a sheltered area (typically the Control Room), while the different satellites units shall be located along the pipeline – placed inside satellite enclosures. (see figure 2)

Figure 2: Pipeline oil leak detection system installation example

For underground installations requiring direct burial, such as pipeline, storage tank, sense cables will have to be run through dedicated plastic slotted pipes (figure 3) to allow cable maintenance (cleaning after leak detection or replacement in case of damage).

Figure 3: Sense cable inside slotted pipe and filtering fabric sleeve

PVC slotted pipe carrying sense

cable running parallel to the pipes

Optional : thick polyethylene sheet

underneath, to collect fuel and

decrease detection time

Figure 4: Example of slotted pipe installation in pipeline application

For storage tank application, the sense cable layout shall be in compliance with the standard API 650 RP 650. (see figures below).

Figure 5: Installation of slotted pipes and sense cables underneath the tank bottom

Figure 6: Installation of slotted pipes and sense cables underneath the tank bottom – Sectional view

Figure 7: Storage tank bottom application: monitoring “grid” composed by sense cable strings disposed in perpendicular rows

Figure 8 Storage tank bottom application: monitoring “grid” composed by sense cable strings disposed in single direction rows

Figure 9: Storage tank bottom application: circumferential monitoring configuration – aerial or underground

FG-ODP
POINT SENSOR

Figure 10: Storage tank floating roof monitoring: example of installation using Point Sensors FG-ODP

All leak detection system components shall be installed in strict accordance with the manufacturer's installation instructions and the distributor’s submittal drawings.

- The installation shall not take place until all construction work to the area of installation is completed, all debris and construction by products have been taken away and the area cleaned.

- The appointed contractor shall ensure that the system is installed by the manufacturer’s trained partner who shall create as built drawings. A site map prepared from the leak detection supplier’s "as built" drawings shall be furnished by the equipment supplier after completion of the installation. The map shall indicate the location of the cable, connectors, and landmarks such as equipment, piping access ports, change of cable direction, and cable distance readings per manufacturer's instructions. Copies of the map drawing shall be provided to the engineer, the owner, and a laminated display version shall be mounted near the alarm module.

- Manufacturer

The Digital Oil Leak Detection system shall be manufactured by:

TTK S.A.S.

19 rue du Général Foy	Tel: +33.1.56.76.90.10

75008 Paris		Fax: +33.1.55.90.62.15

France

Websites: 			http://www.ttk.fr,
 				http://www.ttkuk.com,
				http://www.ttkasia.com,

http://www.ttkusa.com 
				http://www.ttkcanada.com